User Requirements Template

for a BARRIER ISOLATOR AND HVAC SYSTEM

REVISION HISTORY

| Rev. | Date | Approval | Revision Summary |
| --- | --- | --- | --- |
| A1 | 11/06/01 | T. Petro | Draft |
| A2 | 01/15/02 | T. Petro | Incorporated content and changes from review by JETT break-out group on 11/15/01. |
| B1 | 3/1/02 | M Casey | Validation review |
| C1 | 11/20/02 | M Rivera | Format Review |
| C2 | 11/26/02 | T. Petro | Final review of content and format by author |
| 0 | 11/26/02 | T. Petro | Approved for Initial Release |

Table of Contents

1.0	Introduction	5

2.0	Overview	5

3.0	Operational Requirements	6

3.1	Capacity	6

3.2	Process Requirements	6

3.3	Process Control	6

3.4	Functions	7

3.5	Data and Security	9

3.6	Environment	11

4.0	Constraints	14

4.1	Milestones and Timelines	14

4.2	Equipment Constraints	15

4.3	Compatibility and Support	15

4.4	Availability	17

4.5	Procedural Constraints	17

4.6	Maintenance	19

5.0	Life-Cycle	19

5.1	Development	19

5.2	Testing	19

5.3	Delivery	20

5.4	Support	21

6.0	Glossary	22

7.0	References	23

8.0	Approval	24

Project No.:

Insert the unique project number associated with this particular URS.

Document No.:

Insert the Document Identification Number and Revision.

Document Description:

Insert description of document, e.g. PURE STEAM GENERATOR, JETT Example User Requirements Specification.

# Introduction

Note:  Insert your own description and introduction.  You may wish to include your own requirements and specifics to allow the inexperienced reader, contractors, and suppliers adequate explanation to understand the scope of the equipment.

Describe who produced the document, under what authority, and for what purpose.

Describe the contractual status of the document.  Include or reference as an attachment the “legal” paragraph that communicates purchasing terms and conditions in this section.

Describe the relationship of this document to other documents.  This is important for equipment that is part of an integrated process or line and will help the Supplier to understand and ask questions that may otherwise be overlooked.

Refer to the Equipment Validation Plan that outlines the Supplier’s responsibilities is attached.

Remove any options that are not applicable for this project, if other uses will apply list each separately.

This is to be utilized as a guide for the user to answer the majority of questions involved in specifying the “what” for the equipment.  Addendums may be used to round out the requirements.

# Overview

The Barrier Isolator and HVAC System provides a mechanical separation between the controlled room environment, and the interior environment in which the pharmaceutical product is processed.  The barrier isolator is manufactured in such a manner that the materials are resistant to corrosion, do not allow pooling of the cleaning materials, and allow access to the interior as required by the equipment and products.  The environment inside  the barrier isolator is controlled in a manner to allow the pharmaceutical product to be processed in accordance with the purpose and product requirements.

## USE

The equipment shall be used primarily for:

- Continuous Production

- Batch Production

- Other

## EQUIPMENT CLASSIFICATION

For example:

For providing an aseptic environment for:

- Liquid filling of vials with stoppers

- Powder filling of vials with stoppers

- Liquid filling of ampoules with flame-off

- Liquid filling of cartridges with plugs

- Liquid filling of syringes

- Other (define)

Insert your Equipment Classifications here as required using the above example as a guide.

## CLEANING REQUIREMENTS

- Wipedown

- Manual Washdown

- Clean-In-Place (CIP)

- Special Requirements: 
– Peracetic Acid
– Ethylene Oxide
– Chlorine Dioxide
– Vaporized Hydrogen Peroxide 
– Others

## LANGUAGE REQUIREMENTS

- English

- Other (Specify):  ____________________

- Bilingual?  Yes  /  No

# Operational Requirements

## PERFORMANCE REQUIREMENTS

### Capacity

Add capacities and details concerning equipment capacity here.  Identify the type and dimensions of the equipment that will fit inside of the barrier.

## FUNCTIONS

### The Barrier Isolator and HVAC System is divided into two main portions:  The barrier isolator, and the HVAC system.

### Barrier Isolator Operation

The barrier isolator is an enclosure that provides isolation between the operator/outside environment and the interior of the barrier where the pharmaceutical processing is done.  The barrier isolator provides the following functions:

- Isolation between the operator and the process

- Safety Barrier to separate the operator from equipment hazards

- A non-corrosive, drainable, and easily cleaned enclosure.

- Doors to provide access to the equipment during cleaning and changeover

- Gloveports to allow access to machinery and product during production

- Transfer ports to introduce commodities and equipment to the environment

- Infeed opening to introduce commodities to the system.

- Exit opening to allow finished commodities to exit the system.

### Barrier Isolator Design

### The barrier isolator design will meet current GMP for aseptic product manufacture, along with wash down and sanitization requirements.

- All interior corners will have a minimum of __0.5”_ radius.

- Drain pans will have a minimum of __0.5”__ slope per 12” of run.

- Horizontal surfaces will be minimized to resist pooling. Pooling of more than __5ml__ of liquid is not allowed.  Pooled liquid must not be more than __2mm__ deep

- Drain pans shall   terminate in tank bottom drain valves with materials and finish equivalent to the rest of the barrier isolator interior.

- Air distribution from the plenum will use __dual perforated plates__.

- The air distribution system will be removable for cleaning.

#### Safety of the operator from the machinery or processes within the barrier isolator must be ensured.

- All doors will have dual-redundant safety switches that will immediately stop all machinery or processes when the door is opened.

- Gloveports will be guarded with light curtains to immediately stop machinery.

- All moving machinery external to the barrier isolator will be fully guarded and alarmed.

- All high temperature components external to the barrier isolator will be fully guarded and alarmed.

#### Materials and Finish of the Barrier Isolator will meet current GMP’s.

- Wall thickness of the barrier isolator will be a minimum of __7gauge_ Stainless Steel

- Interior surfaces of the barrier isolator will be manufactured from __316L________ Stainless Steel.

- Exterior surfaces of the barrier isolator and ductwork will be manufactured from        __304 or316L___ Stainless Steel.

- Interior finish of the barrier isolator will be  of _______40_ micro-inch Ra finish maximum.

- Exterior finish of the barrier isolator will be  of ______120_ micro-inch Ra finish maximum.

- All interior surfaces will be electro-polished redundant? How else do you get #4 and #5?.

- All welds will be ground and polished to the above finish requirements.

- Air plenums must meet the same materials and finish requirements as the barrier isolator.

- The completed interior of the barrier isolator will be passivated prior to shipment to the site.

- Components attached to the exterior of the barrier isolator must meet current GMP’s and be finished to resist corrosion.

#### Doors and Windows in the barrier isolator allow visibility and access to the interior.

- The window material is manufactured from __tempered safety glass or polycarbonate__.

- The window sealing material is extruded from __silicone rubber__.

- Window seals must be designed to prevent pooling.

- Doors must hinge open to allow access to the interior.

- Doors must be removable without tools.

#### Mousehole Opening(s) are provided at the exit point to allow the exit of good vials and of reject vials.

- Mousehole covers are manufactured to the same requirements as the barrier Isolator.

- Mousehole cover presence is to be sensed and alarmed.

#### Gloveports are provided in the barrier isolator to allow operator access to the interior without compromising sterility.

- Gloves must be replaceable.

- Gloves must be sanitized without absorbing sterilant.

- Gloves will be made from __fabric reinforced PVC__.

- Gloves will be located to access common intervention points.

- Gloves will be positioned to allow access by operators within the normal range of physical sizes.

#### Transfer Ports will be provided to allow component and product entry into the interior of the barrier isolator without compromising  sterility.

- Transfer ports will be located at the following locations, and are of the following sizes:
Location #1:   ___upstream of filler__	__350mm__
Location #2:   ___at stopper entry____	__270mm__
Location #3:   ___at outfeed________	__270mm__
Location #4:   ___N/A____________	__________

- Transfer port manufacture is _____________________

- Transfer port sanitization process is _______________

#### Commodity/Product Infeed to the interior of the barrier isolator will be provided in the design.

Vials enter the barrier isolator from a __depyrogenation tunnel__.

Product enters the barrier isolator through a __bulkhead fitting__.

Stoppers enter the barrier isolator through __transfer port #2____.

Miscellaneous Devices such as:__tools, SMA stands, hangers, platforms, instrumentation, test ports, etc.___

#### Product Exit from the interior of the barrier isolator will be provided in the design.

Vial path #1 transfers vials to a __flat belt conveyor__.

Vial path #2 transfers vials to a __22” transfer disk__.

Drains in the bottom of the barrier isolator are provided at __7__ points to allow for liquids to be removed during changeover and sanitization.

Drains must be closed during production.

### HVAC System Operation

### The HVAC system controls the environment inside  the isolator, and provides the following functions:

- Pressure differential between the interior and exterior of the isolator

- Temperature control of the interior

- Humidity Control of the interior

- Air Circulation through the interior

- HEPA/ULPA filtration of the interior air

- Sanitation of the barrier isolator and the equipment This seems incorrect, it may maintain sanitation but not induce it.

#### Pressure Differential between the interior and exterior is maintained at positive   0.10”H2O, +/- 0.02”H2O.  Pressure balance is to be maintained within these parameters under all conditions of:

Product infeed doors open or closed

Product entering or not entering

Exit door open or closed

Product exiting or not exiting

Multiple withdrawals of glove ports

Transition of transfer ports

Fluctuation of outside environment within tolerance

#### Temperature Control is maintained at +/- 1.0(C of setpoint within the full temperature control range of 5.0(C minimum to 50(C maximum.  Temperature control is to be maintained within these parameters under all conditions of:

- Beginning of the batch

- Long term continuous run of the batch

- Fluctuation of outside environment within tolerance

#### Humidity Control during production is maintained at +/- 1.0(C dew point within the full humidity range of 5.0(C minimum to 25(C maximum. The system is designed to only lower the dew point.  There are no provisions to raise the dew point above that of the ambient environment. Humidity control is to be maintained within these parameters under all conditions.

- Drying of the barrier isolator after cleaning

- Beginning of the batch

- Long term continuous run of the batch

- Fluctuation of outside environment with tolerance

#### Air Circulation is provided by a variable speed fan circulating the air through heating, cooling, dehumidification, and filter systems.  The air is forced into the barrier isolator through a perforated plate to disperse the air throughout the interior uniformly.  Air is then returned from the interior through the return air ducts.  Airflow is measured 12 inches below the perforated plates, and must be between 50 feet per second minimum to 90 feet per second maximum.  Air circulation levels are to be maintained within these levels under all conditions.

- Sanitizing cycle of the barrier isolator

- Beginning of the batch

- Long term continuous run of the batch

- Fluctuation of outside environment with tolerance

#### HEPA/ULPA filtration of the recirculated air is provided by two pairs of filters in series.  The filters are 99.99% efficient at removing particles greater than 0.3 microns in size.  The fresh air inlet uses a roughing filter and a 90% efficient ASHRAE filter prior to the HEPA/ULPA filters.  Recirculated air filtration at all times that the HVAC fan is operating (fragment).

#### Sanitization of the Barrier is provided by the following processes:

- The interior of the barrier isolator is manually/automatically cleaned out of any debris from the previous production.  All areas of the interior that can accumulate debris must be accessible to allow for removal of debris.

- The interior surfaces of the barrier isolator are able to be wiped down by cleaning personnel easily and efficiently without danger to the personnel or damage to the materials.

- The interior of the barrier isolator can be washed down with cleaning agents and water without pooling or deterioration of the interior surfaces.

- The interior surfaces of the barrier isolator are drainable without excessive pooling to allow rapid drying of the interior.

- Cleaning agents are introduced by injection into the HVAC system through a port in the ductwork after the filters.

- The interior surfaces of the barrier isolator can be sanitized by _______________ cleaning agents without damage to the surfaces of the barrier isolator.

- All interior surfaces of the barrier isolator are reached by the sanitization agents.

### Power Failure and Recovery

### On power failure, the system shall fail into a “safe state.”  On power restoration, the system shall not restart without operator or communication-link input.

Insert your specific power failure / recovery scheme here. For example:

In the event of a power failure, the system shall protect in the following priority:

- Personnel

- Equipment

- Product

Recovery Methods:

Insert your specific recovery scheme here. For example:

- Manually re-start based on operator inputs.  (Operator initiates power recovery sequence)

- Re-start based on last state before loss of power.  (System runs through power recovery sequence when operator start signal is given)

- If there is an automatic batch reporting system, the information shall be retained in the event of a power failure  (A UPS is required for automatic batch reporting systems for data retention).

### Emergency Stop

Insert your specific E-Stop strategy and communication scheme here. For example:

The system shall have an E-Stop system designed to shut down all environmental controls in a safe manner. The E-Stop will be Hard-wired into the filler E-Stop system so that all machinery within the barrier/isolator will stopp immediately upon actuation of any E-Stop button.  Determine if the HVAC fan will also stop under an emergency stop.  The E-Stop button(s) shall be located in easily accessible areas around the equipment as required by local safety standards.

### Alarms And Warnings

Insert your Alarm scheme here. For example:

#### “Critical alarms” shall take action automatically to shut the equipment down and notify the operator.  The operator shall be required to acknowledge the alarm before the alarm can be reset and the system restarted.  Once the alarm is reset, the operator may restart the system.

#### “Non-Critical alarms” shall take action to shut the equipment down at the end of the cycle, and notify the operator once stopped.  The operator shall be required to acknowledge the alarm before the alarm can be reset and the system restarted.  Once the alarm is reset, the operator may restart the system.

#### “Operator Alert” shall notify the operator and take no further action. Non-Critical warnings and shall sound the alarm horn, illuminate the alarm indicator but allow the system to continue to operate.  The operator shall be required to acknowledge the warning in order to silence the alarm horn, and the alarm indicator shall be extinguished when the warning condition disappears.

The Equipment shall have the following alarms and warnings:

| Alarm or Warning | Critical | Non-Critical |
| --- | --- | --- |
| Emergency Stop | X |  |
| Control Platform Communication Watchdog | X |  |
| Control Power Fault | X |  |
| Barrier Door Open | X |  |
| Glove Port Light Curtain Interrupted | X |  |
| Mousehole Cover Open | X |  |
| Mousehole Cover Closed | X |  |
| Drain Valve Failed to Open | X |  |
| Drain Valve Failed to Close | X |  |
| Light Curtain Contamination Fault |  | X |
| Recirculation Fan Failed to Start | X |  |
| Filter Differential Pressure Alarm |  | X |
| Barrier High Pressure Alarm | X |  |
| Barrier Low Pressure Alarm | X |  |
| Barrier Differential pressure alarm | X |  |
| PLC Battery Low |  | X |
| Other Alarms as Required |  |  |

## Data and Security

### Interfaces

Insert your interface scheme here. For example:

The Programmable Logic Controller / Operator-Interface Panel system (hereafter referred to as the “PLC/OIP system”) shall include interfaces with the Operator, Supervisors, external equipment, and the User’s control system to ensure safe, reliable, continuous, and automatic operation and easy, safe, and reliable configuration.

This section should address the following issues:

  - Operator interface access levels

  - Frequency of data point collection

  - Hardcopy/electronic data collection requirements

  - Compliance with 21CFR Part 11 (for Europe - EREC Guidelines)

  - Data retention time on the system

  - Data storage media

Include the operator interface access levels, e.g. what functions can be access by operators, which only by supervisors, maintenance personnel, etc.

Access to all Input/Output values and system status bits shall be provided through a data-communication link.  Security for data and operator access is provided by (Check all that apply):

- User ID/Password

- Card Reader

- Biometric (Fingerprint, eye scan, voice recognition, etc.)

### Interface with Supervisors and Operators

Insert your interface scheme here. For example:

The PLC/OIP system shall include interfaces with the Operator that ensures easy, safe, and reliable operation.

An operator-interface panel shall be provided and mounted on the machine.  This panel shall provide the necessary switches, indicators, and devices to operate the barrier isolator HVAC system.  The following shall be displayed:

- System Status (e.g., “state” the system currently is in)

- Pressure Differential

- Temperature

- Humidity

- HVAC Fan Speed

- Utility Controls

- Alarms and Warnings.

- Other (specify).

Delete any of the listed functions/indications that are not applicable for this application and add additional functions/indications as required.

#### The following shall be accessible only to Supervisors:

Security Configurations

Control loop variables (i.e., “PID terms”).

Ability to force system to a different state.

Alarm setpoints.

Other ____________  (specify).

### Interface with Other Equipment

Insert your interface scheme here. Describe, define or give details where possible. For example:

Delete any of the listed interfaces that are not applicable for this application and add additional interfaces as required.

The control system shall include the interfaces necessary to facilitate operation and configuration.

Interface to other equipment may include:

- Processing equipment interior to the barrier isolator HVAC system

- Commodity infeed systems

- Commodity outfeed systems

- Exterior HVAC system

- Cleaning and sanitization systems

- MES or SCADA systems

- Others:

For example:

An RS-232 communications port shall be provided.

A Modem communications port shall be provided.

A high-speed configuration/monitoring connection shall be provided.

### Data Collection

- None

- Recorder

- Process Printout

- Electronic process printout, Historical Trending

- Electronic process printout, Historical Trending and interface to company network

The following shall be recorded:

Differential Pressure

Temperature

Humidity

Pressure Leak Test Rates

Other:  ____________________   (Specify)

## ENVIRONMENT

In the following section, provide details of the physical environment in which equipment will be operated.

### Layout

For example:

Allocated floor space for the barrier isolator is _______ inches wide by ________ inches in length, with at least a 36 inch corridor around the periphery for the equipment.  Vertical clearance is _________ inches.

Allocated floor space for the HVAC package is _______ inches by ________ inches with at least a 36 inch corridor around the periphery for the equipment.  Vertical clearance is _________ inches.

The HVAC package will be:

- Mounted directly to the top of the barrier isolator.

- Mounted along side (at the same level) as the barrier isolator.

- Mounted indirectly above the barrier isolator.

- Other

See attached drawing #________________________ (if applicable).

Note:  Layout is specific to the size equipment being used and system requirements of the equipment.

### Physical Conditions

For Example(s):

The barrier isolator and HVAC system will be used for (Check all that apply, insert your equipment requirements here):

- Aqueous

- Low LEL (Lower Explosion Limit) Solvents

- High LEL Solvents

- Other

Room Classification:

- Room will be non-hazardous (Zone 0)

- Room will be Class I Div II (Zone 1) (explosive atmosphere present at known times)

- Room will be Class I Div I  (Zone 2) (explosive atmosphere present at all times)

Clean Room Classification:

- Class A

- Class B

- Class C

- Other

Biohazard Level:

- BL-1

- BL-2

- Etc.

NEMA Rating of enclosures:

NEMA 12 (Oil tight)

NEMA 4 (Wash down)

NEMA 4X (Wash down and non-Corrosive)

#### Intended Operating Environment:

The Equipment shall be mounted in a GMP environment with a temperature range of 15 to 25 °C, non-condensing humidity.

Vibration levels are:

- Negligible

- Slight

- Severe

Seismic Zone:

- Negligible

- Slight

- Severe

Noise Constraints:  (Note:       Place in Constraint section)

85 DB from 3 feet

EMI / RFI levels are:

- Negligible.

- Other (specify) _________.

The equipment is to be used at the following environmental conditions:

Altitude ________ ft above sea level.

The following is applicable for HVAC Equipment:

Process air enters in from:

- Indoor   Temperature ______(C

- Outdoor   Temperature: Minimum: ______( C,  Maximum: ______(C

Climatic conditions:

Winter dry bulb ______(C

Winter wet bulb ______(C

Summer dry bulb _____(C

Summer wet bulb _____(C

(If these values are not known, state location to be installed: ) ___________________________________

#### Containment   (move to  constraints)

##### Explosion Protection

Note:  This section is only valid if processing products with a risk of explosion.  Select one choice.

- 2 Bar Construction with isolation and suppression

- 10 Bar construction with isolation only

- Closed-Loop Nitrogen System

##### Containment of Product

Note:  This section is only valid if the product being used is highly reactive.

Insert containment guidelines here.

# Constraints

## Milestones and Timelines

Based on the model outlined below, establish the project milestones with a timeline:

## Compatibility and Support

Include any requirements for compatibility with other User systems.  In the examples provided below, fill in blanks with the appropriate information.  Delete areas that are not applicable to this application.

### CONTROL PLATFORM Controllers

The Supplier shall utilize 		 Control Platform Controllers that shall include a communications port.

The Supplier shall provide documentation that the program (embedded software) was developed and coded utilizing 			 program development and documentation software.

The supplier shall indicate the use of custom or “bespoke” code within the equipment, and shall supply licensing of the custom code for the life of the equipment.

An escrow agreement shall be required in the event the supplier cannot support the supplied custom software any longer.  In such instances, the source code and all information regarding the source code shall be given to the user in a timely fashion to prevent downtime of the equipment.

### Preferred Vendor List

If necessary attach any critical preferred vendors.  Refrain from driving the supplier into customizing his equipment package.

If the vendor wishes to deviate from the Preferred Instrumentation List, a listing of the proposed components and instrumentation sub-vendors indicating type and model numbers shall be submitted with the quotation, along with an explanation of why the deviation is recommended.

### Utilities

The utilities and space involved needs to be discussed prior to purchasing the equipment.  Obviously, the actual equipment size is but a small part of the entire scope of work necessary to implement a larger system. The unit and its support equipment must be able to be installed in current building facilities.

The User shall ensure that the following utilities are available and that the utility supply lines and piping are terminated with fittings or connections, which are compatible with those described on the Customer Connection Drawings.

The Supplier shall specify utility data, which is marked with a triangle.  Utility data, which are not specified or marked with a triangle, shall be brought to the attention of the User.  These data shall be specified (by the User or the Supplier) and shall be approved by both the User and the Supplier before system design begins.

Base Utilities Worksheet:

(Electricity:

______ VAC   ____ Hertz

- Single Phase

- Three Phase

(Uninterruptible Power Supply Required?  Yes  /  No

To Power:  Entire System   /   Controls Only

(Instrument Air:

_______  PSIG  (Must be clean, dry ISA instrument quality air, capacity to be determined by size of equipment)  Recommend at least 90 PSIG constant air pressure for all equipment unless specified.

(Chilled Water:

________  GPH,   ________  PSIG,   ________(C  Closed loop with supply and return connections.  (can be provided with additives for corrosion resistance if required by the facility,  not sanitary)

(Fresh Air Inlet:

________  inch diameter air inlet.  (can enter from technical area)  Temperature of inlet air must be within the same range as required of the machinery.

(Exhaust Air:

________  inch diameter air exhaust port.  (Provisions must be made for treatment of exhausted air depending on the product and/or sterilant being used in the system.)

(Sanitary Water:

________  GPH,   _________  PSIG,   ________(C  (Used for wash down (CIP) of the interior of the barrier isolator)

(Sterilant:

Define the method of sanitization, the delivery system, and the rate sized for the interior volume of the barrier isolator.  Not normally supplied as a direct connect utility system.

(HVAC Drain:

________  inch diameter  (for draining condensate from the cooling coils of the HVAC system)

(Barrier Isolator Drain:

________  inch diameter   Quantity of _______  drains at various locations throughout the barrier isolator.  Tank bottom welded valves that are installed with the same specifications as the tank bottoms (redundant sentence).

(Other utility requirements shall be discussed as needed.

In the following section, provide details of the physical environment requirements for the system.  Items that are listed and that are not applicable should be deleted from the document.  Provide additional details as necessary.

## Availability

The [equipment/system] is intended to be operated [Continuously, Regularly, __ hours per day,  __ hours per week].

Operation of the [equipment/system] shall be suspended, and the system shall be available for preventative maintenance or routine service [__ hours per week, __ continuous hours per week, __ days per month, __ weeks per year].

## Procedural Constraints

### Product Contact Materials

Describe any local procedural requirements such as local standards, which must be adhered to if applicable.

All piping welds and product contact welds shall meet ASME and 3A specification requirements.  Product contact metal to be (316L Stainless Steel, 316 Stainless Steel, 304 Stainless Steel, etc.)

List critical requirements for surface finish, roughness, etc..

Other standards are attached.  The Supplier shall adhere to the indicated sections only.

### Product in Contact with Materials

All product contact parts should be considered.  The [equipment/system] will be used for (aqueous solutions, low LEL (lower explosion limit) solvents, high LEL solvents, etc.). redundant see 3.4.2

What is the difference between this section and 4.4.1?

### Noise Level Constraints

Insert your own noise level constraint requirements here.

For example:

The noise level generated during operation of the [equipment/system] will not exceed 85 dB from 3 feet away.

### EMI / RFI levels are:

Insert your own electrical and radio noise immunity requirements here.

For example:

The [equipment/system] [will/will not] be used in an area where two-way radio communication devices are in operation.  The [equipment/system] shall meet CE requirements for electrical noise immunity and emissions.

### Containment

#### Explosion Protection

This section is only valid if the product being used is highly reactive.  Insert containment guidelines here (i.e. Bar Construction with isolation and suppression, 10 Bar construction with isolation only, Closed-Loop Nitrogen System, etc.).

### Labeling

All equipment and control wiring shall be labeled and identified.

## Maintenance

Describe the expected hardware and software maintenance support including:  ease of maintenance, expansion capability (software only), likely enhancements (software only), expected lifetime and long-term support.

System shall be maintained on a schedule as indicated by the supplier.  Supplier is to provide (at minimum) the following maintenance instructions:

- All sub-systems provided (Maintenance and operation manuals of vendor equipment)

- A comprehensive lubrication list and recommended lubrication schedule

- A comprehensive recommended maintenance (regular recommended inspection intervals, wear points, recommended spare parts list)

- Supplier shall supply ______ Copies of Operation, Installation, Maintenance and de-commissioning manuals

# Life-Cycle

## Development

If S88 is to be applied to the equipment being acquired, it should be referenced in this section of the document.

The Supplier shall provide a Quality and Project Plan as part of their proposal.  The Supplier shall have a quality system in place.  Internal quality procedures shall be available for the User’s review.

The Supplier shall provide a Project Manager for the project to provide a single communication point with the User.

The project shall utilize the GAMP methodology when developing the system and documentation.

## Testing

Describe the Supplier testing requirements.  Reference the Validation Test Plan, Factory Acceptance Test, special tests, etc.  This section should also include required amount of demonstrated run time, any special materials necessary to complete testing, integration testing, etc.

In order to verify system performance, the User shall witness the execution of the Factory Acceptance Test procedures.  The Supplier shall notify the User _______ weeks in advance of the start of this test.

The Factory Acceptance Test Specification shall be submitted to the User for review and approval prior to execution.  A minimum of _______ weeks shall be allowed for the User to review and to comment and/or approve the Factory Acceptance Test Specification.

Refer to the Equipment Validation Plan for applicable procedures.

## Delivery

The [equipment/system], with all options, equipment, and the documentation listed below, shall be delivered to the User’s receiving dock.

### Documentation

Installation, operation, and maintenance instruction documentation for the system shall be developed to a level that is comprehensible to a high school graduate.

The Supplier shall use the formats described in the GAMP Supplier Guide, Current Version, to produce the documentation.  The Supplier shall provide the documentation for preliminary review.  The Supplier shall provide documentation reflecting “as-built” condition with final delivery.

All final documents shall be shipped with transmittals that identify them as contractually required documents.  All final documents and drawings shall reflect “as-built” condition.

All documents shall in the language of the destination country and supplied with hard copies and electronic versions supplied in the format identified for each document:

User should define format for document transmission (ie. MS Word, Autocad, etc.)  Below is an example:

- Project Plan	Microsoft Word 97 (*.doc)

- User Requirements Specification	Microsoft Word 97 (*.doc)

- Functional Specification/Requirements	Microsoft Word 97 (*.doc)

- Design Specifications	Microsoft Word 97 (*.doc)

- Controls Test 	Microsoft Word 97 (*.doc)

- Hardware Installation Test	Microsoft Word 97 (*.doc)

- Operational Test	Microsoft Word 97 (*.doc)

- Factory Acceptance Test	Microsoft Word 97 (*.doc)

- Operator, Maintenance and Service Manuals	Microsoft Word 97 (*.doc)

- Process and Instrumentation Diagram (P&ID)	AutoCAD version 12.0 (*.dxf)

- Instrument Listing	Microsoft Word 97 (*.doc) or Excel 97 (*.xls)

- Control Schematics	AutoCAD version 12.0 (*.dxf)

- Control Panel Assembly Drawings	AutoCAD version 12.0 (*.dxf)

- Equipment Assembly Drawings	AutoCAD version 12.0 (*.dxf)

- Bill of Materials	Microsoft Word 97 (*.doc) or Excel 97 (*.xls)

- Spare Parts List	Microsoft Word 97 (*.doc) or Excel 97 (*.xls)

- Component Cut Sheets	Microsoft Word 97 (*.doc) or Excel 97 (*.xls)

- CONTROL PLATFORM Program 
Printout and Disk File	XXX Program Development format

- OIP Configuration Printout and Disk File	XXX Program Development format

## Support

Describe what support activities are required after acceptance.  The paragraphs outlined below provide some areas for consideration.

### Start-up Support (list available options)

#### Training (list training options available)

### Post Start-up Support (list post-startup support available)

#### Technical Support

Telephone (Voice or Modem)

Replacement Parts Availability List (Normal lead times shall be listed)

#### User Site Support

Preventative Maintenance (list maintenance contracts available)

System Improvements (supplier shall notify user of any improvements available on a regular basis)

# Glossary

If necessary, attach a glossary, which includes definitions of terms that may be unfamiliar to the Supplier or terminology that may have meanings specific to entries on this User Requirements Check sheet.

For example (example list is not intended to be complete):

| Acronym | Definition |
| --- | --- |
| (C | Degrees Celsius |
| BL | Biohazard Level |
| CFR | Code of Federal Regulations |
| dB | Decibels |
| EMI | Electro-Magnetic Interference |
| ft | Feet |
| GUI | Graphic User Interface |
| HMI | Human – Machine Interface |
| HVAC | Heating, Ventilation, and Air Conditioning |
| ISO | International Organization for Standardization |
| JETT | Joint Equipment Transition Team |
| LEL | Lower Explosion Limit |
| OIP | Operator Interface Panel |
| RFI | Radio Frequency Interference |
| URS | User Requirement Specification |
|  | Table is incomplete |

# References

List references that were used in preparing this document or that provide additional details, such as:

  - Equipment Validation Plan

  - Current revision of GAMP Guidelines

  - Vendor Piping Certification (if applicable)

  - Customer Connection Diagram

  - Approved Instrumentation List

  - Process Flow Diagram

  - 21 CFR Part 11

  - National Electric Code

  - S88

# Approval

Insert your company’s standard approval page at the appropriate position in the document or utilize the sample approvals listed below.  The approval process/requirements should be outlined in the Equipment Validation Plan.

| This document has been reviewed by the User Project Manager and approved for use by the Supplier. |
| --- |
| Printed/Typed Name |  | Signature |  | Date |
| This document has been reviewed by the User Quality Assurance Group and approved for use by the Supplier. |
| Printed/Typed Name |  | Signature |  | Date |
| This document has been reviewed by the Supplier Project Manager and approved for use by the Supplier Project Team. |
| Printed/Typed Name |  | Signature |  | Date |

Other approvals as necessary may be included, such as the Technical Services Groups, User Groups, Engineering, etc. as required.